***Emergency Eyewash and Shower Equipment***

|  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | LOCATION |  |  |  | DESCRIPTION |  |
|  |  |  |  |  |  |  |  |  |  |
| UNIT |  | BLOCK |  | TAG NUMBER |  | TYPE OF EQUIPMENT |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
| HAZARD |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | SHOWER |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | DOESN’T |
| DESCRIPTION |  | PERFORMANCE REQUIREMENTS | COMPLIES | COMPLY |
|  |  |  |  |  |  |  |  |  |
| Shower Height |  |  |  | Not less than 82" not more than 96" from standing level |  |  |
|  |  |  |  |  |  |  |  |
| Water Spray Pattern |  | 20" minimum diameter—60" from standing level |  |  |
|  |  |  |  |  |  |  |  |  |
| Center of Water Spray |  | 16" from any obstruction |  |  |  |
|  |  |  |  |  |  |  |  |
| Water Delivery—Potable |  | Minimum of 20 gpm/meeting water spray pattern |  |  |
|  |  |  |  |  |  |  |  |
| Control Valve and Actuator |  | Stay ON type—Off to ON one second—easily located |  |  |
|  |  |  |  |  |  |  |  |  |
| Location to Hazard |  | Maximum 10 seconds from hazard |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
| Identification |  |  |  | Well lighted, sign, highly visible |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | EYE/FACE WASH |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | DOESN’T |
| DESCRIPTION |  | PERFORMANCE REQUIREMENTS | COMPLIES | COMPLY |
|  |  |  |  |  |  |  |  |
| Water Delivery—Potable |  | Minimum of 3 gpm—dual stream flushing |  |  |
|  |  |  |  |  |  |  |  |  |  |
| Velocity |  |  |  | Soft spent stream |  |  |  |
|  |  |  |  |  |  |  |  |  |
| Location to Hazard |  | Maximum 10 seconds from hazard |  |  |  |
|  |  |  |  |  |  |  |  |  |
| Nozzles |  |  |  | Covers to protect from airborne contaminants |  |  |
|  |  |  |  |  |  |  |  |  |
| Nozzle Height |  |  |  | Not less than 33" not more than 45" from standing level |  |  |
|  |  |  |  |  |  |  |  |
| Control Valve and Actuator |  | Stay ON type—Off to ON one second—easily located |  |  |
|  |  |  |  |  |  |  |  |  |  |
| Identification |  |  |  | Well lighted, sign, highly visible |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | DRENCH HOSE |  |  |  |
|  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | DOESN’T |
| DESCRIPTION |  | PERFORMANCE REQUIREMENTS | COMPLIES | COMPLY |
|  |  |  |  |  |  |  |  |  |
| Water Delivery—Potable |  | Minimum of 3 gpm—low velocity |  |  |  |
|  |  |  |  |  |  |  |  |  |
| Location to Hazard |  | Maximum 10 seconds or from hazard |  |  |  |
|  |  |  |  |  |  |  |  |  |
| Control Valve |  |  |  | OFF to ON one second—easy to locate and operate |  |  |
|  |  |  |  |  |  |  |  |  |  |