Energized Electrical Work Assessment

| Work Request (To be completed by the person requesting the review.) |
| --- |
| Work site location: (building & room number) |  | Work order/project no.: |  |
| Planned start date/time: |  | Planned end date/time: |  |
| Description of the work to be performed: |  |
| Equipment requested to be shut down: (specify how long) |  |
|  | Until work is complete Temporarily, while barriers are being placed |
| Requested by: | Signature: | Title: | Date: |
| Hazard Analysis (To be completed by the electrically qualified persons doing the work.) |
| Shock Analysis/Approach Boundaries: Limited approach boundary- Restricted approach boundary- Prohibited approach boundary- | (from Table 130.2(C)) _____ft _____in _____ft _____in Work will be conducted within this boundary. _____ft _____in Work will be conducted within this boundary. |
| Results of the flash hazard analysis - | The flash protection boundary is 4 ft 0 in for systems that are 600 volts or less based on the product of clearing times of 6 cycles (0.1 second) and the available bolted fault current of 50 kA or any combination not exceeding 300 kA cycles (500 ampere seconds). Calculation results: _____ft _____in |
| Hazard/risk category for the task: ATPV rating (in cal/cm2) for FR clothing: | 0 1 2 3 4 (from Table 130.7(C)(9)(A) & (11)) N/A (Cat 0) 4 (Cat 1) 8 (Cat 2) 25 (Cat 3) 40 (Cat 4) |
| Voltage-rated tools Voltage-rated gloves Safety glasses Hearing protection Leather gloves Leather work shoes Hard hat Hard hat FR liner (ATPV) | Short-sleeve shirt (nat fiber) Long-sleeve shirt (nat fiber) Long pants (natural fiber) Long-sleeve FR shirt (ATPV) Long FR pants (ATPV) FR coveralls (ATPV) FR jacket/rainwear (ATPV) | Multi-layer FR flash suit jacket (ATPV) Multi-layer FR flash suit pants (ATPV) Arc-rated face shield (ATPV) Flash suit hood (ATPV) (from Table 130.7(C)(10) |
| Means employed to restrict the access of unqualified persons from the work area: | Signs/tags Barricades Attendants |
| Has a documented job briefing with detailed procedures been conducted? | Yes, see attached No |
| Do you agree that the work described above can be done safely? | Electrically Qualified Person(s) | Date |
| Justification for the live work request: | Shut down creates an increased/additional hazard (specify): _________________________________________________ Shut down is infeasible due to design or operational limitations (specify): _________________________________ |
| The next available date for shutdown is: |  |
| Request for energized electrical work: | Electrical qualified person: | Date: |
| Proposed Energized Electrical Work Review (To be completed by Departmental Management.) |
| Proposed energized electrical work has been reviewed by: | Supervisor: | Date: |
|  | Safety Representative: | Date: |
|  | Departmental Management: | Date: |